SEWS 10.4.1 (1 of 4)	Sheet 1 of ______

SCREENING EVALUATION WORK SHEET (SEWS)

Equipment ID No.:

Equipment Class: HVAC Ducts

HVAC line identification:

System:

Building:

Floor El. (s):

Location:

Operating Pressure:

PSIG

Inches of water

Performance Category:

Duct System Boundary

Description or sketch (attach sheets as necessary):

Functionality Requirement

1.	During seismic event	Y	N	U

2.	After seismic event	Y	N	U

Structural Integrity Review (Section 10.4.1)

1.	Duct free of damage, defects, and degradation	Y	N	U	N/A

2.	Industry standard duct material and  stiffeners are utilized	Y	N	U	N/A

3.	Industry standard duct joints are utilized	Y	N	U	N/A

4.	Support spans satisfy the criteria	Y	N	U	N/A

5.	Ducts are properly tied-down to the supports	Y	N	U	N/A

6.	Heavy in-line equipment is adequately restrained	Y	N	U	N/A

7.	Appurtenances are positively attached to duct	Y	N	U	N/A

8.	No stiff branch with flexible header	Y	N	U	N/A

9.	No other concerns	Y	N	U	N/A

Are the above caveats met?	Y	N	U

SEWS 10.4.1 (2 of 4)	Sheet 2 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: HVAC Ducts

HVAC line identification:

System:

Pressure Boundary Integrity Review (Section 10.4.1)

Is any pressure boundary integrity required?	Y	N	U

If the answer to the above question is NO, SKIP THIS SECTION

1.	Duct joints are rugged	Y	N	U	N/A

2.	Stiffener spacings are within the guidelines	Y	N	U	N/A

3.	Bolted flanged joints satisfy SMACNA (Tables G and H) requirements	Y	N	U	N/A

4.	No point supported round duct	Y	N	U	N/A

5.	Flexible bellows can accomodate motions	Y	N	U	N/A

6.	No additional concerns	Y	N	U	N/A

Are the above caveats met?	Y	N	U

Support Review (Section 10.4.1)

1.	Beam Clamps are oriented to preclude slipping off the support, channel	Y	N	U	N/A

nuts have teeth or ridges, and no cast-iron inserts 	Y	N	U	N/A

2.	Support memeber capacity exceeds demand 	Y	N	U	N/A

3.	Does the anchorage appear adequate?	Y	N	U	N/A

4.	No broken or obviously defective hardware

5.	No additional concerns	Y	N	U	N/A

Are the above caveats met?	Y	N	U

Interaction Effects (Chapter 7)

1.	Soft targets free from impact by nearby equipment
	   or structures	 		Y	N	U	N/A

2.	If equipment contains sensitive essential relays, equipment free
	   from all impact by nearby equipment or structures 	Y	N	U	N/A

3.	Attached lines have adequate flexibility  	Y	N	U	N/A

4.	No collapse of overhead equipment, distribution systems,

or masonry walls 		Y	N		N/A

5.	Equipment is free from credible and significant

seismic-induced flood and spray concerns	Y	N		N/A

6.	No credible seismic-induced fire concerns	Y	N		N/A

7.	No other Òtwo over oneÓ concerns as defined in DOE-STD-1021	Y	N		N/A

8.	No other concerns 		Y	N	U	N/A

Is equipment free of interaction effects? 		Y	N	U

SEWS 10.4.1 (3 of 4)	Sheet 3 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: HVAC Ducts

HVAC line identification:

System:

Bounding Candidate Evaluation

Duct is not a candidate for bounding calculations 	Y	N	U	N/A

Discussion:

Analytical Review

SEWS 10.4.1 (4 of 4)		Sheet 4 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: HVAC Ducts

HVAC line identification:

System:

Comments

Screening Walkdown(s):

Date	Time	Team Members

Recommend Resolution

q	Maintenance action:

q	Further evaluation:

q	Retrofit design:

q	Other:

q	No further action required.  Equipment is seismically adequate.

All aspects of the equipment's seismic adequacy have been addressed.

Evaluation by:  			Date:

(All team members)