SEWS 8.1.1 (1 of 4)	Sheet 1 of ______

SCREENING EVALUATION WORK SHEET (SEWS)

Equipment ID No.:

Equipment Class: Batteries on Racks

Equipment description:

System:

Equipment Location: Bldg.

Floor El.

Room, Row/Col.

Manufacturer, model, etc.:

Battery type:

Individual Battery Weight:

Drawing No.:

Performance Category:

Functionality Requirement

q	Contact Lead Relay Reviewer to determine if item contains Essential Relays

q	For components whose function or structural integrity is required, complete all sections of this form.

q	For all other components, only anchorage evaluation is required.

Seismic Capacity vs. Demand (Chapter 5)

1.	Seismic Capacity based on:

q	Reference Spectrum

q	GERS

q	Existing documentation

2.	Elevation where equipment receives seismic input

Seismic Demand Spectrum (SDS) based on:

q	In-structure response spectrum (IRS) per DOE-STD-1020

q	Other in-structure response spectrum (determine appropriate experience data

scale factor)

q	Design basis earthquake (DBE) per DOE-STD-1020

q	Other

Scale Factor (SF)			Experience Data Factor (FED)

Does capacity exceed demand?	Y	N	U

Reference:

Caveats (Section 8.1.1)

Reference Spectrum (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below)

1.	Equipment is included in earthquake experience equipment class 	Y	N	U	N/A

2.	Plates of the cells are lead-calcium flat-plate, PlantŽ or of
	   Manchex design		Y	N	U	N/A

3.	Each individual battery weighs less than 450 lbs	Y	N	U	N/A

4.	Close-fitting, crush-resistant spacers fill two-thirds of
	   vertical space between cells 	Y	N	U	N/A

5.	Cells restrained by end and side rails	Y	N	U	N/A

SEWS 8.1.1 (2 of 4)	Sheet 2 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: Batteries on Racks

Equipment description:

Caveats (Cont.)

6.	Racks have longitudinal cross bracing	Y	N	U	N/A

7.	Wood racks evaluated to industry accepted standards 	Y	N	U	N/A

8.	Batteries greater than 10 years old specifically evaluated

for aging effects		Y	N	U	N/A

9.	Have you looked for and found no other adverse concerns? 	Y	N	U	N/A

Is the intent of all the caveats met for Reference Spectrum? 	Y	N	U	N/A

GERS (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below)

1.	Equipment is included in generic seismic testing equipment class 	Y	N	U	N/A

2.	Meets all Reference Spectrum caveats	Y	N	U	N/A

3.	Plates of the cells are lead-calcium flat-plate design
	   (i.e., not Manchex design)		Y	N	U	N/A

4.	Batteries supported on two-step racks or single-tier racks;

restrained by double side and end rails which are symmetrically

located with respect to the cell center-of-gravity	Y	N	U	N/A

Is the intent of all the caveats met for GERS? 	Y	N	U	N/A

Anchorage (Chapter 6)

1.	Type of anchorage:

q 	expansion anchor

q 	cast-in-place bolt or headed stud anchor

q 	cast-in-place J-bolt

q 	grouted-in-place bolt

q 	welds to embedded steel on exposed steel

q 	lead cinch anchors

q	Other

q 	N/A (no further anchorage considerations)

2.	Appropriate characteristics for anchorage type checked

(size, location, equipment characteristics)	Y	N	U

3.	Gap at threaded anchor less than 1/4 inch	Y	N	U 	N/A

4.	Base stiffness and no significant prying action requirements met	Y	N	U

5.	Equipment base strength and structural load path adequate	Y	N	U

6.	Embedment steel and pads requirements met	Y	N	U 	N/A

7.	Embedment length requirements met	Y	N	U

8.	Anchor spacing requirements met	Y	N	U

9.	Edge distance requirements met	Y	N	U

10.	Concrete strength requirements met	Y	N	U

SEWS 8.1.1 (3 of 4)	Sheet 3 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: Batteries on Racks

Equipment description:

Anchorage (Cont.)

11.	Concrete crack requirements met	Y	N	U

12.	Equipment with essential relays requirements met	Y	N	U 	N/A

13.	Installation adequacy requirements met	Y	N	U 	N/A

14.	No other concerns	Y	N	U

Does anchorage capacity exceed demand?	Y	N	U

Reference:

Interaction Effects (Chapter 7)

1.	Soft targets free from impact by nearby equipment
	   or structures	 		Y	N	U	N/A

2.	If equipment contains sensitive essential relays, equipment free
	   from all impact by nearby equipment or structures 	Y	N	U	N/A

3.	Attached lines have adequate flexibility  	Y	N	U	N/A

4.	No collapse of overhead equipment, distribution systems,

or masonry walls 		Y	N		N/A

5.	Equipment is free from credible and significant

seismic-induced flood and spray concerns	Y	N		N/A

6.	No credible seismic-induced fire concerns	Y	N		N/A

7.	No other Òtwo over oneÓ concerns as defined in DOE-STD-1021	Y	N		N/A

8.	No other concerns 		Y	N	U	N/A

Is equipment free of interaction effects? 		Y	N	U

Comments

SEWS 8.1.1 (4 of 4)	Sheet 4 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: Batteries on Racks

Equipment description:

Comments (Cont.)

Screening Walkdown(s):

Date	Time	Team Members

Recommend Resolution

q	Maintenance action:

q	Further evaluation:

q	Retrofit design:

q	Other:

q	No further action required.  Equipment is seismically adequate.

All aspects of the equipment's seismic adequacy have been addressed.

Evaluation by:  			Date:

(All team members)