SEWS 8.2.8 (1 of 3)	Sheet 1 of ______

SCREENING EVALUATION WORK SHEET (SEWS)

Equipment ID No.:

Equipment Class: Engine-Generators

Equipment description:

System:

Equipment Location: Bldg.

Floor El.

Room, Row/Col.

Manufacturer, model, etc.:

Weight:

Drawing No.:

Performance Category:

Functionality Requirement

q	Contact Lead Relay Reviewer to determine if item contains Essential Relays

q	For components whose function or structural integrity is required, complete all sections of this form.

q	For all other components, only anchorage evaluation is required.

Seismic Capacity vs. Demand (Chapter 5)

1.	Seismic Capacity based on:

q	Reference Spectrum

q	GERS

q	Existing documentation

2.	Elevation where equipment receives seismic input

Seismic Demand Spectrum (SDS) based on:

q	In-structure response spectrum (IRS) per DOE-STD-1020

q	Other in-structure response spectrum (determine appropriate experience data

scale factor)

q	Design basis earthquake (DBE) per DOE-STD-1020

q	Other

Scale Factor (SF)			Experience Data Factor (FED)

Does capacity exceed demand?	Y	N	U

Reference:

Caveats (Section 8.2.8)

Reference Spectrum (Identify with an asterisk (*) those caveats which are met by intent without meeting the specific wording of the caveat rule and explain the reason for this conclusion in the COMMENTS section below)

1.	Equipment is included in earthquake experience equipment class 	Y	N	U	N/A
2.	Driver and driven equipment connected by a rigid support or
	   common skid 		Y	N	U	N/A
3.	Have you looked for and found no other adverse concerns? 	Y	N	U	N/A

Is the intent of all the caveats met for Reference Spectrum? 	Y	N	U	N/A

SEWS 8.2.8 (2 of 3)	Sheet 2 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: Engine-Generators

Equipment description:

Anchorage (Chapter 6)

1.	Type of anchorage:

q 	expansion anchor

q 	cast-in-place bolt or headed stud anchor

q 	cast-in-place J-bolt

q 	grouted-in-place bolt

q 	welds to embedded steel on exposed steel

q 	lead cinch anchors

q	Other

q 	N/A (no further anchorage considerations)

2.	Appropriate characteristics for anchorage type checked

(size, location, equipment characteristics)	Y	N	U

3.	Gap at threaded anchor less than 1/4 inch	Y	N	U 	N/A

4.	Base stiffness and no significant prying action requirements met	Y	N	U

5.	Equipment base strength and structural load path adequate	Y	N	U

6.	Embedment steel and pads requirements met	Y	N	U	N/A

7.	Embedment length requirements met	Y	N	U

8.	Anchor spacing requirements met	Y	N	U

9.	Edge distance requirements met	Y	N	U

10.	Concrete strength requirements met	Y	N	U

11.	Concrete crack requirements met	Y	N	U

12.	Equipment with essential relays requirements met	Y	N	U 	N/A

13.	Installation adequacy requirements met	Y	N	U 	N/A

14.	No other concerns	Y	N	U

Does anchorage capacity exceed demand?	Y	N	U

Reference:

Interaction Effects (Chapter 7)

1.	Soft targets free from impact by nearby equipment
	   or structures	 		Y	N	U	N/A
2.	If equipment contains sensitive essential relays, equipment free
	   from all impact by nearby equipment or structures 	Y	N	U	N/A
3.	Attached lines have adequate flexibility  	Y	N	U	N/A
4.	No collapse of overhead equipment, distribution systems,
	   or masonry walls 		Y	N		N/A
5.	Equipment is free from credible and significant
	   seismic-induced flood and spray concerns	Y	N	U	N/A
6.	No credible seismic-induced fire concerns	Y	N		N/A

7.	No other Òtwo over oneÓ concerns as defined in DOE-STD-1021	Y	N		N/A

8.	No other concerns 		Y	N	U	N/A

Is equipment free of interaction effects? 		Y	N	U

SEWS 8.2.8 (3 of 3)	Sheet 3 of ______

SCREENING EVALUATION WORK SHEET (SEWS) (Cont.)

Equipment ID No.:

Equipment Class: Engine-Generators

Equipment description:

Comments

Screening Walkdown(s):

Date	Time	Team Members

Recommend Resolution

q	Maintenance action:

q	Further evaluation:

q	Retrofit design:

q	Other:

q No further action required. Equipment is seismically adequate.

All aspects of the equipment's seismic adequacy have been addressed.

Evaluation by:  			Date:

(All team members)